## Sheet1
Fault Name | Fault Description | Fault Syntax
Chiller Poor Staging | If the active plant part load is less than an acceptable value, then the fault will flag. (25%) | IF(TRUEFORDURATION( <<CHW_LOAD>>/(<<CH_1_ENA>>*600 + <<CH_2_ENA>>*600 + <<CH_3_ENA>>*120) < 0.25, "01:00:00")) THEN 1 ELSE 0
Condenser 24/7 Loop High Supply Setpoint | If the condenser 24/7 loop setpoint is not below an acceptable value, then the fault will flag. (34) | IF(TRUEFORDURATION( <<CNDW_MAIN_SWT_STP>> > 34, "01:00:00")) THEN 1 ELSE 0
Condenser 24/7 Loop Low Differential Temperature | If the differential temperature is lower than an allowable value, then the fault will flag. (dT 4) | IF(TRUEFORDURATION( <<CNDW_MAIN_RWT>> - <<CNDW_MAIN_SWT>> < 4 , "01:00:00")) THEN 1 ELSE 0
Condenser 24/7 Loop Pump Over-Staging | If either the source-side or load-side has both condenser pumps operating at once, then the fault will flag. | IF(TRUEFORDURATION((<<CNDWP_1_STS>> == 1 && <<CNDWP_2_STS>> == 1 ) ¦¦ (<<CNDWP_7_STS>> == 1 && <<CNDWP_8_STS>> == 1), "00:30:00")) THEN 1 ELSE 0
Condenser Water High Supply Setpoint | If the condenser water system setpoint is not below an acceptable value, then the fault will flag. (26) | IF(TRUEFORDURATION( <<CNDW_SWT_STP>> > 26, "01:00:00")) THEN 1 ELSE 0
Failed Chilled Water Differential Pressure Sensor | If chilled water differential pressure sensor is reading outside of the typical range, then faulth will flag. | IF( TRUEFORDURATION(( <<CHW_DP>> <= 0 ¦¦ <<CHW_DP>> > 400), "00:30:00")) THEN 1 ELSE 0
Failed Chilled Water Return Temperature Sensor | If the chilled water return water temparature is reading outside a typical range, then fault will flag. | IF( TRUEFORDURATION(( <<CHW_RWT>> <= 0 ¦¦ <<CHW_RWT>> > 50), "00:30:00")) THEN 1 ELSE 0
Failed Chilled Water Supply Temperature Sensor | If the chilled water supply water temparature is reading outside a typical range, then fault will flag. | IF( TRUEFORDURATION(( <<CHW_SWT>> <= 0 ¦¦ <<CHW_SWT>> > 50), "00:30:00")) THEN 1 ELSE 0
Failed Chiller 1&2 Return Water Temperature Sensor | If the chiller 1&2 return water temperature sensor is reading outside the typical range, then fault will flag. | IF( TRUEFORDURATION(( <<CH_1_2_RWT>> <= 0 ¦¦ <<CH_1_2_RWT>> > 50), "00:30:00")) THEN 1 ELSE 0
Failed Chiller 1&2 Supply Water Temperature Sensor | If the chiller 1&2 supply water temperature sensor is reading outside the typical range, then fault will flag. | IF( TRUEFORDURATION(( <<CH_1_2_SWT>> <= 0 ¦¦ <<CH_1_2_SWT>> > 50), "00:30:00")) THEN 1 ELSE 0
Failed Chiller Chilled Water Flow Sensor | If any of the chilled water flow sensor on the chillers is reading outside of typical range, then fault will flag. | IF( TRUEFORDURATION(( <<CH_1_CHW_FLOW>> <= 0 ¦¦ <<CH_1_CHW_FLOW>> > 5000 ¦¦ <<CH_2_CHW_FLOW>> <= 0 ¦¦ <<CH_2_CHW_FLOW>> > 5000 ¦¦ <<CH_3_CHW_FLOW>> <= 0 ¦¦ <<CH_3_CHW_FLOW>> > 5000), "00:30:00")) THEN 1 ELSE 0
Failed Condenser Warer Supply Temperature Sensor | If the condenser water supply water temparature is reading outside a typical range, then fault will flag. | IF( TRUEFORDURATION(( <<CNDW_SWT>> <= 0 ¦¦ <<CNDW_SWT>> > 70), "00:30:00")) THEN 1 ELSE 0
Failed Condenser Water Make-Up Flow Sensor | If the condenser water make-up flow sensor is reading outside a typical range, then fault will flag. | IF( TRUEFORDURATION(( <<CNDW_MU_FLOW>> <= 1 ¦¦ <<CNDW_MU_FLOW>> > 5000), "00:30:00")) THEN 1 ELSE 0
Failed Condenser Water Return Temperature Sensor | If the condenser water return water temparature is reading outside a typical range, then fault will flag. | IF( TRUEFORDURATION(( <<CNDW_RWT>> <= 0 ¦¦ <<CNDW_RWT>> > 70), "00:30:00")) THEN 1 ELSE 0
Failed Heat Exchanger Supply Water Temperature Sensor | If the heat exchanger supply water temperature sensor is reading outside the typical range, then fault will flag. | IF( TRUEFORDURATION(( <<HX_SWT>> <= 5 ¦¦ <<HX_SWT>> > 120), "00:30:00")) THEN 1 ELSE 0
Failed Outdoor Air Temperature Sensor | If the outside air temperature sensor is reading outside the typical range, then the fault will flag. | IF( TRUEFORDURATION(( <<OAT>> <= -15 ¦¦ <<OAT>> > 45), "00:30:00")) THEN 1 ELSE 0
Chiller In Hand | If the chiller is commanded off but proving on, then the fault will flag. (AMP 10) | IF(TRUEFORDURATION( <<AMP>> > 10 && <<CMD>> == 0, "01:00:00")) THEN 1 ELSE 0
Failed CHW Flow sensor | If the chilled water flow sensor is reading outside the typical range then the fault will flag. | IF( TRUEFORDURATION((<<CHW_FLOW>> < 100 ¦¦ <<CHW_FLOW>> > DESIGN_CHW_FLOW * 1.15),"01:00:00")) THEN 1 ELSE 0
Failed CHW Return Temperature Sensor | If the chilled water return temperature sensor is reading outside the typical range, then the fault will flag. | IF( TRUEFORDURATION( (<<CHW_RWT>> <= 0 ¦¦ <<CHW_RWT>> > 50), "01:00:00")) THEN 1 ELSE 0
Failed CHW Supply Temperature Sensor | If the chilled water supply temperature sensor is reading outside the typical range, then the fault will flag. | IF( TRUEFORDURATION( (<<CHW_SWT>> <= 0 ¦¦ <<CHW_SWT>> > 50 ), "01:00:00")) THEN 1 ELSE 0
Failed CNDW Flow sensor | If the condenser water flow sensor is reading outside the typical range, then the fault will flag. | IF( TRUEFORDURATION(( <<CNDW_FLOW>> < 100 ¦¦ <<CNDW_FLOW>> > <<DESIGN_CNDW_FLOW>> * 1.15),"01:00:00")) THEN 1 ELSE 0
Failed CNDW Return Tempereture sensor | If the condenser water return temperature sensor is reading outside the typical range, then the fault will flag. | IF( TRUEFORDURATION( (<<CNDW_RWT>> <= 0 ¦¦ <<CNDW_RWT>> > 50), "01:00:00")) THEN 1 ELSE 0
Failed CNDW Supply Temperature sensor | If the condenser water supply temperature sensor is reading outside the typical range, then the fault will flag. | IF( TRUEFORDURATION( (<<CNDW_SWT>> <= 0 ¦¦ <<CNDW_SWT>> > 50 ), "01:00:00")) THEN 1 ELSE 0
Low Chilled Water Supply Temperature Setpoint | If the chiller is producing colder water than required, then the fault will flag. (5.5) | IF(TRUEFORDURATION( <<CHW_SWT_STP>> < 5.5 &&<<CMD>> == 1, "00:30:00")) THEN 1 ELSE 0
Low Condenser Differential Temperature | If the condenser differential temperature is lower than a threshold value, then the fault will flag. (dT 50%, FLOW 50%) | IF(TRUEFORDURATION( <<CNDW_RWT>> - <<CNDW_SWT>> < <<Design_CNDW_LWT>>*0.5 - <<Design_CNDW_EWT>>*0.5 && <<CNDW_FLOW>> > <<Design_CNDW_FLOW>>*0.5, "01:00:00")) THEN 1 ELSE 0
Low Evaporator Differential Temperature | If the evaporator differential temperature is lower than an allowable value, then the fault will flag. (dT 50%, FLOW 50%) | IF(TRUEFORDURATION( <<CHW_RWT>> - <<CHW_SWT>> < <<DESIGN_CHW_EWT>>*0.5 - <<DESIGN_CHW_LWT>>*0.5 && <<CHW_FLOW>> > <<DESIGN_CHW_FLOW>>*0.5, "01:00:00")) THEN 1 ELSE 0
Over-Cooling | If the chiller is producing water significantly colder than the setpoint requires, then the fault will flag. (dT 3, AMP 10) | IF(TRUEFORDURATION( <<CHW_SWT_STP>> - <<CHW_SWT>> > 3 && <<CMD>> == 1 && <<AMP>> > 10, "01:00:00")) THEN 1 ELSE 0
Poor Chiller Efficiency | If the chiller is operating at a poor efficiency (significantly greater than design) then the fault will flag. (AMP 10, EFF 0.65) | IF(TRUEFORDURATION( 343*<<AMP>>/391/<<CHW_LOAD>> > 0.65 && <<AMP>> > 10 , "01:00:00")) THEN 1 ELSE 0
Short Cycling | If the chiller has too many starts in a 24-hour period, then the fault will flag. (4) | IF(TRUEFORDURATION( <<DAILY_ STARTS>> > 4, "00:30:00")) THEN 1 ELSE 0
Surge Condition | If the condenser flow rate and lift do not unload nearly evenly, then the fault will flag. Surge will cause major chiller maintenance issues. | IF(TRUEFORDURATION(( <<CNDW_RWT>> - <<CHW_SWT>>)/(<<Design_CNDW_LWT>> - <<Design_EVAP_LWT>>) - <<CNDW_FLOW>>/<<Design_CNDW_FLOW>> > 0.1 && <<AMP>> > 10 , "00:30:00")) THEN 1 ELSE 0
Chiller In Hand | If the chiller is commanded off but proving on, then the fault will flag. | IF(TRUEFORDURATION( <<STS>> > == 1 && <<CMD>> == 0, "01:00:00")) THEN 1 ELSE 0
Failed CHW Flow sensor | If the chilled water flow sensor is reading outside the typical range then the fault will flag. | IF( TRUEFORDURATION((<<CHW_FLOW>> < 100 ¦¦ <<CHW_FLOW>> > DESIGN_CHW_FLOW * 1.15),"01:00:00")) THEN 1 ELSE 0
Failed CHW Return Temperature Sensor | If the chilled water return temperature sensor is reading outside the typical range, then the fault will flag. | IF( TRUEFORDURATION( (<<CHW_RWT>> <= 0 ¦¦ <<CHW_RWT>> > 50), 3600000)) THEN 1 ELSE 0
Failed CHW Supply Temperature Sensor | If the chilled water supply temperature sensor is reading outside the typical range, then the fault will flag. | IF( TRUEFORDURATION( (<<CHW_SWT>> <= 0 ¦¦ <<CHW_SWT>> > 50 ), 3600000)) THEN 1 ELSE 0
Failed CNDW Flow sensor | If the condenser water flow sensor is reading outside the typical range, then the fault will flag. | IF( TRUEFORDURATION(( <<CNDW_FLOW>> < 100 ¦¦ <<CNDW_FLOW>> > <<DESIGN_CNDW_FLOW>> * 1.15),"01:00:00")) THEN 1 ELSE 0
Failed CNDW Return Tempereture sensor | If the condenser water return temperature sensor is reading outside the typical range, then the fault will flag. | IF( TRUEFORDURATION( (<<CNDW_RWT>> <= 0 ¦¦ <<CNDW_RWT>> > 50), 3600000)) THEN 1 ELSE 0
Failed CNDW Supply Temperature sensor | If the condenser water supply temperature sensor is reading outside the typical range, then the fault will flag. | IF( TRUEFORDURATION( (<<CNDW_SWT>> <= 0 ¦¦ <<CNDW_SWT>> > 50 ), 3600000)) THEN 1 ELSE 0
Failed Open Evaporator Isolation Valve | If the evaporator isolation valve is commanded closed but there is still measurable flow through the evaporator, then the fault will flag. (FLOW 10, VLV 5) | IF(TRUEFORDURATION( <<CHW_FLOW>> > 10 && <<CHW_ISO_VLV CMD>> < 5, "01:00:00")) THEN 1 ELSE 0
Low Chilled Water Supply Temperature Setpoint | If the chiller is producing colder water than required, then the fault will flag. (8) | IF(TRUEFORDURATION( <<CHW_SWT_STP>> < 8 && <<CMD>> == 1, "00:30:00")) THEN 1 ELSE 0
Low Evaporator Differential Temperature | If the evaporator differential temperature is lower than an allowable value, then the fault will flag. (dT 50%, FLOW 50%) | IF(TRUEFORDURATION( <<CHW_RWT>> - <<CHW_SWT>> < <<DESIGN_CHW_EWT>>*0.5 - <<DESIGN_CHW_LWT>>*0.5 && <<CHW_FLOW>> > <<DESIGN_CHW_FLOW>>*0.5, "01:00:00")) THEN 1 ELSE 0
Over-Cooling | If the chiller is producing water significantly colder than the setpoint requires, then the fault will flag. (dT 3) | IF(TRUEFORDURATION( <<CHW_SWT_STP>> - <<CHW_SWT>> > 3 && <<CMD>> == 1 && <<STS>> == 1, "01:00:00")) THEN 1 ELSE 0
Short Cycling | If the chiller has too many starts in a 24-hour period, then the fault will flag. (4) | IF(TRUEFORDURATION( <<DAILY_STARTS>> > 4, "00:30:00")) THEN 1 ELSE 0
Failed Closed Bypass Valve | If the valve is commanded open but proving closed, then the fault will flag. | IF(TRUEFORDURATION( <<BYP_VLV_CMD>> == 1 && <<BYP_VLV_STS>> == 0, "01:00:00")) THEN 1 ELSE 0
Failed Closed Inlet Isolation Valve | If the valve is commanded open but proving closed, then the fault will flag. | IF(TRUEFORDURATION( <<IN_VLV_CMD>> == 1 && <<IN_VLV_STS>> == 0, "01:00:00")) THEN 1 ELSE 0
Failed Closed Outlet Isolation Valve | If the valve is commanded open but proving closed, then the fault will flag. | IF(TRUEFORDURATION( <<OUT_VLV_CMD>> == 1 && <<OUT_VLV_STS>> == 0, "01:00:00")) THEN 1 ELSE 0
Failed Fan | If the unit is commanded on but failing to prove, then the fault will flag. (PCT 25%, FREQ 5) | IF(TRUEFORDURATION( <<UNIT_CMD>> == 1 && <<SPD_PCT>> >25 && <<SPD_FREQ>> < 5, "00:30:00")) THEN 1 ELSE 0
Failed Heat Exchanger Source Side Leaving Water Temperature Sensor | If the heat exchanger source side leaving water temperature sensor is reading outside of a typical range, then fault will flag. | IF( TRUEFORDURATION(( <<HX_SS_LWT>> <= 0 ¦¦ <<HX_SS_LWT>> > 70), "00:30:00")) THEN 1 ELSE 0
Failed Open Bypass Valve | If the valve is commanded closed but proving open, then the fault will flag. | IF(TRUEFORDURATION( <<BYP_VLV_CMD>> == 0 && <<BYP_VLV_STS>> == 1, "01:00:00")) THEN 1 ELSE 0
Failed Open Inlet Isolation Valve | If the valve is commanded closed but proving open, then the fault will flag. | IF(TRUEFORDURATION( <<IN_VLV_CMD>> == 0 && <<IN_VLV_STS>> == 1, "01:00:00")) THEN 1 ELSE 0
Failed Open Outlet Isolation Valve | If the valve is commanded closed but proving open, then the fault will flag. | IF(TRUEFORDURATION( <<OUT_VLV_CMD>> == 0 && <<OUT_VLV_STS>> == 1, "01:00:00")) THEN 1 ELSE 0
Failed Sump Water Temperature Sensor | If the sump water temperature sensor is reading outside of a typical range, then fault will flag. | IF( TRUEFORDURATION(( <<SMPT>> <= 0 ¦¦ <<SMPT>> > 70), "00:30:00")) THEN 1 ELSE 0
Failed Supply Water Temperature Sensor | If the supply water temperature sensor is reading outside of a typical range, then fault will flag. | IF( TRUEFORDURATION(( <<SW_T>> <= 0 ¦¦ <<SW_T>> > 70), "00:30:00")) THEN 1 ELSE 0
Fan in Hand | If the unit is commanded off but proving on, then the fault will flag. (FREQ 5) | IF(TRUEFORDURATION( <<UNIT_CMD>> == 0 && <<SPD_FREQ>> > 5, "00:30:00")) THEN 1 ELSE 0
Manual Override - Pump Speed | If the unit is overcooling the water and not at minimum speed, or is undercooling the water but not near maximum speed, then the fault will flag. (dT 3, PCT 35% 95%) | IF(TRUEFORDURATION(( <<HX_SS_LWT_STP>> - <<HX_SS_LWT>> > 3 && <<SPD_PCT>> > 35 ¦¦ <<HX_SS_LWT>> - <<HX_SS_LWT_STP>> > 3 && <<SPD_PCT>> < 95 ) && <<UNIT_CMD>> == 1, "01:00:00")) THEN 1 ELSE 0
Over-Cooling | If the unit is overcooling the water and the fan is near minimum speed, then the fault will flag. (dT 3, PCT 35%) | IF(TRUEFORDURATION( <<HX_SS_LWT_STP>> - <<HX_SS_LWT>> > 3 && <<SPD_PCT>> < 35 && <<UNIT_CMD>> == 1, "01:00:00")) THEN 1 ELSE 0
Under-Cooling | If the unit is undercooling the header and the fan is near maximum speed, then the fault will flag. (dT 15, PCT 95%) | IF(TRUEFORDURATION( <<HX_SS_LWT>> - <<HX_SS_LWT_STP>> > 15 && <<SPD_PCT>> > 95 && <<UNIT_CMD>> == 1, "01:00:00")) THEN 1 ELSE 0
Valve Control Mismatch | If the bypass valve and outlet valve are given the same command, then the fault will flag. | IF(TRUEFORDURATION( <<OUT_VLV_CMD>> == 1 && <<BYP_VLV_CMD>> == 1 ¦¦ <<OUT_VLV_CMD>> == 0 && <<BYP_VLV_CMD>> == 0, "00:30:00")) THEN 1 ELSE 0
Failed Control Reset - Supply Fan Speed | If the pump speed is not resetting, then the fault will flag. (RANGE 20%, PCT 50%) | IF(TRUEFORDURATION(<<STS>>==1 && <<SPD_PCT>> > 50 && (timesincelastchange(<<SPD_PCT>>, 5, “00:05:00”)>fromhours(1))), "01:00:00") THEN 1 ELSE 0
Failed Pump | If the pump is commanded on but failing to prove, then the fault will flag. (AMP 0.5) | IF(TRUEFORDURATION( <<UNIT_CMD>> == 1 && <<UNIT_AMP>> < 0.5, "00:30:00")) THEN 1 ELSE 0
Fan in Hand | If the pump is commanded off but proving on, then the fault will flag. | IF(TRUEFORDURATION( <<UNIT_CMD>> == 0 && <<STS>> == 1, "00:30:00")) THEN 1 ELSE 0
Failed Differential Pressure Sensor | If the differential Pressure Sensor is reading outside a typical range, then fault will flag. | IF( TRUEFORDURATION(( <<DB>> <= -10 ¦¦ <<DB>> > 500), "00:30:00")) THEN 1 ELSE 0
Failed Pump | If the pump is commanded on but failing to prove, then the fault will flag. (AMP 0.5) | IF(TRUEFORDURATION( <<UNIT_CMD>> == 1 && <<UNIT_AMP>> < 0.5, "00:30:00")) THEN 1 ELSE 0
Fan in Hand | If the pump is commanded off but proving on, then the fault will flag. | IF(TRUEFORDURATION( <<UNIT_CMD>> == 0 && <<STS>> == 1, "00:30:00")) THEN 1 ELSE 0
Manual Override - Pump Speed | If the pump is overpressurizing the header and not at minimum speed, or is underpressurizing the header but not near maximum speed, then the fault will flag. (dP 15, PCT 35% 95%) | IF(TRUEFORDURATION( (<<DP>> - <<DP_STP>> > 15 && <<SPD_PCT>> > 35 ¦¦ <<DP_STP>> - <<DP>> > 15 && <<SPD_PCT>> < 95 ) && <<UNIT_CMD>> == 1 && <<STS>> == 1, "01:00:00")) THEN 1 ELSE 0
Over-Pressurization | If the pump is overpressurizing the header and the pump is near minimum speed, then the fault will flag. (dP 15, PCT 35%) | IF(TRUEFORDURATION( <<DP>> - <<DP_STP>> > 15 && <<SPD_PCT>> < 35 && <<UNIT_CMD>> == 1 && <<STS>> == 1 , "01:00:00")) THEN 1 ELSE 0
Under-Pressurization | If the pump is underpressurizing the header and the pump is near maximum speed, then the fault will flag. (dP 15, PCT 95%) | IF(TRUEFORDURATION( <<DP_STP>> - <<DP>> > 15 && <<SPD_PCT>> > 95 && <<UNIT_CMD>> == 1 && <<STS>> == 1, "01:00:00")) THEN 1 ELSE 0
Failed Heat Exchanger Load Side Leaving Water Temperature Sensor | If the heat exchanger load side leaving water temperature sensor is reading outside a typical range, then fault will flag. | IF( TRUEFORDURATION(( <<HX_LS_LWT>> <= 0 ¦¦ <<HX_LS_LWT>> > 120), "00:30:00")) THEN 1 ELSE 0
Failed Pump | If the pump is commanded on but failing to prove, then the fault will flag. (AMP 0.5) | IF(TRUEFORDURATION( <<UNIT_CMD>> == 1 && <<UNIT_AMP>> < 0.5, "00:30:00")) THEN 1 ELSE 0
Fan in Hand | If the pump is commanded off but proving on, then the fault will flag. | IF(TRUEFORDURATION( <<UNIT_CMD>> == 0 && <<STS>> == 1, "00:30:00")) THEN 1 ELSE 0
Manual Override - Pump Speed | If the pump is overcooling the water and not at minimum speed, or is undercooling the water but not near maximum speed, then the fault will flag. (dT 3, PCT 35% 95%) | IF(TRUEFORDURATION( (<<HX_LS_LWT_STP>> - <<HX_LS_LWT>> > 3 && <<SPD_PCT>> > 35 ¦¦ <<HX_LS_LWT>> - <<HX_LS_LWT_STP>> > 3 && <<SPD_PCT>> < 95 ) && <<UNIT_CMD>> == 1 && <<STS>> == 1, "01:00:00")) THEN 1 ELSE 0
Over-Cooling | If the pump is overcooling the water and the pump is near minimum speed, then the fault will flag. (dT 3, PCT 35%) | IF(TRUEFORDURATION( <<HX_LS_LWT_STP>> - <<HX_LS_LWT>> > 3 && <<SPD_PCT>> < 35 && <<UNIT_CMD>> == 1 && <<STS>> == 1 , "01:00:00")) THEN 1 ELSE 0
Under-Cooling | If the pump is undercooling the header and the pump is near maximum speed, then the fault will flag. (dT 15, PCT 95%) | IF(TRUEFORDURATION( <<HX_LS_LWT>> - <<HX_LS_LWT_STP>> > 15 && <<SPD_PCT>> > 95 && <<UNIT_CMD>> == 1 && <<STS>> == 1, "01:00:00")) THEN 1 ELSE 0
Failed Heat Exchanger Source Side Leaving Water Temperature Sensor | If the heat exchanger source side leaving water temperature sensor is reading outside a typical range, then fault will flag. | IF( TRUEFORDURATION(( <<HX_SS_LWT>> <= 0 ¦¦ <<HX_SS_LWT>> > 120), "00:30:00")) THEN 1 ELSE 0
Failed Pump | If the pump is commanded on but failing to prove, then the fault will flag. (AMP 0.5) | IF(TRUEFORDURATION( <<UNIT_CMD>> == 1 && <<UNIT_AMP>> < 0.5, "00:30:00")) THEN 1 ELSE 0
Fan in Hand | If the pump is commanded off but proving on, then the fault will flag. | IF(TRUEFORDURATION( <<UNIT_CMD>> == 0 && <<STS>> == 1, "00:30:00")) THEN 1 ELSE 0
Manual Override - Pump Speed | If the pump is overcooling the water and not at minimum speed, or is undercooling the water but not near maximum speed, then the fault will flag. (dT 3, PCT 35% 95%) | IF(TRUEFORDURATION( (<<HX_SS_LWT_STP>> - <<HX_SS_LWT>> > 3 && <<SPD_PCT>> > 35 ¦¦ <<HX_SS_LWT>> - <<HX_SS_LWT_STP>> > 3 && <<SPD_PCT>> < 95 ) && <<UNIT_CMD>> == 1 && <<STS>> == 1, "01:00:00")) THEN 1 ELSE 0
Over-Cooling | If the pump is overcooling the water and the pump is near minimum speed, then the fault will flag. (dT 3, PCT 35%) | IF(TRUEFORDURATION( <<HX_SS_LWT_STP>> - <<HX_SS_LWT>> > 3 && <<SPD_PCT>> < 35 && <<UNIT_CMD>> == 1 && <<STS>> == 1 , "01:00:00")) THEN 1 ELSE 0
Under-Cooling | If the pump is undercooling the header and the pump is near maximum speed, then the fault will flag. (dT 15, PCT 95%) | IF(TRUEFORDURATION( <<HX_SS_LWT>> - <<HX_SS_LWT_STP>> > 15 && <<SPD_PCT>> > 95 && <<UNIT_CMD>> == 1 && <<STS>> == 1, "01:00:00")) THEN 1 ELSE 0
Failed Pump | If the pump is commanded on but failing to prove, then the fault will flag. (AMP 0.5) | IF(TRUEFORDURATION( <<UNIT_CMD>> == 1 && <<UNIT_AMP>> < 0.5, "00:30:00")) THEN 1 ELSE 0
Failled Bypass Flow Sensor | If the bypass flow sensor is reading outside a typical range, then fault will flag. | IF( TRUEFORDURATION(( <<BYP_FLOW>> <= 1 ¦¦ <<BYP_FLOW>> > 20 * <<BYP_FLOW_STP>>), "00:30:00")) THEN 1 ELSE 0
Fan in Hand | If the pump is commanded off but proving on, then the fault will flag. | IF(TRUEFORDURATION( <<UNIT_CMD>> == 0 && <<STS>> == 1, "00:30:00")) THEN 1 ELSE 0
Manual Override - Pump Speed | If the pump is overflowing the header and not at minimum speed, or is underflowing the header but not near maximum speed, then the fault will flag. (dF 25, PCT 35% 95%) | IF(TRUEFORDURATION( (<<BYP_FLOW>> - <<BYP_FLOW_STP>> > 25 && <<SPD_PCT>> > 35 ¦¦ <<BYP_FLOW_STP>> - <<BYP_FLOW>> > 25 && <<SPD_PCT>> < 95 ) && <<UNIT_CMD>> == 1 && <<STS>> == 1, "01:00:00")) THEN 1 ELSE 0
Over-Flow | If the pump is overflowing the header and the pump is near minimum speed, then the fault will flag. (dF 25, PCT 35%) | IF(TRUEFORDURATION( <<BYP_FLOW>> - <<BYP_FLOW_STP>> > 25 && <<SPD_PCT>> < 35 && <<UNIT_CMD>> == 1 && <<STS>> == 1 , "01:00:00")) THEN 1 ELSE 0
Under-Flow | If the pump is underflowing the header and the pump is near maximum speed, then the fault will flag. (dF 25, PCT 95%) | IF(TRUEFORDURATION( <<BYP_FLOW_STP>> - <<BYP_FLOW>> > 25 && <<SPD_PCT>> > 95 && <<UNIT_CMD>> == 1 && <<STS>> == 1, "01:00:00")) THEN 1 ELSE 0